## Slide 1: OX200
ParameterSetup in Profinet

## Slide 2: How to change the Parameter Set-Up
Parameter Set-Ups can be changed via the acyclic communication path
Most PLCs offer build in Functions for that purpose
For a Siemens PLC and the TIA portal you can use the functions RDREC or WRREC for reading and writing acyclic data
For a Beckhoff PLC via the TwinCAT you can use the functions ADSREAD or ADSWRITE for reading and writing acyclic data

## Slide 3: Siemens Tia Portal

## Slide 4: Hardware identifier for subslot

## Slide 5: ParameterSetup value on Connection establishment

## Slide 6: RDREC and WRREC functions

## Slide 7: RDREC and WRREC functions
INDEX = 1 MLEN (length in bytes) = 1

## Slide 8: Tia-Portal manuals
https://support.industry.siemens.com/cs/document/109779999/wo-finden-sie-die-handb%C3%BCcher-und-updates-f%C3%BCr-die-tia-portal-produktversionen-?dti=0&lc=de-WW

## Slide 9: RDREC
You use the instruction "RDREC" to read the data record with the number INDEX from the module addressed using the ID. This may be a module in a central rack or a distributed module (PROFIBUS DP or PROFINET IO).
Use the parameter ID to select from which module (DP/PROFINET IO) a data record is to be read. Use only the hardware identifier of the module for the "ID" parameter.
Use the INDEX parameter to select the information to be read from the module. Which data records can be read with which data record number depends on the module. For additional information, see the manual to the specific module.
The data records readable via "RDREC" have a different length. Use MLEN to specify the maximum number of data record bytes you want to read. If length "0" is selected at the parameter MLEN, the complete data record is written at the parameter RECORD.
The destination area RECORD should have at least the length of MLEN bytes. If you read out the full data record with MLEN=0, use the maximum length of the data record for RECORD. The structure (configuration, data types and length) that you use at the parameter RECORD, also depends on which data record is read out by which module.
The value TRUE for the output parameter VALID indicates that the data record was successfully transferred to the destination area RECORD. In this case, the LEN output parameter contains the length of the read data in bytes.
If an error has occurred during transfer of the data record, this is indicated by the output parameter ERROR. In this case, the output parameter STATUS contains the error information.

## Slide 10: WRREC
The instruction "WRREC" is used to transfer the RECORD data record to the component addressed using ID. This may be a module in a central rack or a distributed component (PROFIBUS DP or PROFINET IO).
Use LEN to specify the length of the data record to be transmitted in bytes. The selected length of the source range RECORD should have at least the length of LEN bytes.
The value TRUE at output parameter DONE indicates that the data record has been successfully transferred.
If an error has occurred during transfer of the data record, this is indicated by the output parameter ERROR. In this case, the output parameter STATUS contains the error information.

## Slide 11: Beckhoff PLC via the TwinCAT

## Slide 12: NetID and Port

## Slide 13: ADS information of parametrization

## Slide 14: ADSREAD and ADSWRITE functions

## Slide 15: Beckhoff manuals
ADSREAD
https://infosys.beckhoff.com/english.php?content=../content/1033/tcplclibsystem/html/TcPlcLibSys_ADSREAD.htm&id
ADSWRITE
https://infosys.beckhoff.com/english.php?content=../content/1033/tcplclibsystem/html/tcplclibsys_adswrite.htm&id

## Slide 16: ADSREAD
NETID : Is a string containing the AMS network identifier of the target device to which the ADS command is directed.
PORT : Contains the port number of the ADS device.
IDXGRP : Contains the index group number (32 bit, unsigned) of the requested ADS service. This value is to be found in the ADS table of the addressed device.
IDXOFFS : Contains the index offset number (32 bit, unsigned) of the requested ADS service. This value is to be found in the ADS table of the addressed device.
LEN : Contains the number, in bytes, of the data to be read.
DESTADDR : Contains the address of the buffer which is to receive the data that has been read. The programmer is himself responsible for dimensioning the buffer to a size that can accept ‘LEN’ bytes. The buffer can be a single variable, an array or a structure, whose address can be found with the ADR operator.
READ : The ADS command is triggered by a rising edge at this input.
TMOUT : States the time before the function is cancelled.
BUSY : This output remains TRUE until the block has executed a command, but at the longest for the duration supplied to the ‘Timeout’ input. While Busy = TRUE, no new command will be accepted at the inputs. Please note that it is not the execution of the service but its acceptance whose time is monitored.
ERR : This output is switched to TRUE if an error occurs during the execution of a command. The command-specific error code is contained in ‘ErrorId’. If the block has a timeout error, ‘Error’ is TRUE and ‘ErrorId’ is 1861 (hexadecimal 0x745). Is reset to FALSE by the execution of a command at the inputs.
ERRID : Contains the command-specific error code of the most recently executed command. Is reset to 0 by the execution of a command at the inputs.

## Slide 17: ADSWRITE
NETID : Is a string containing the AMS network identifier of the target device to which the ADS command is directed.
PORT : Contains the port number of the ADS device.
IDXGRP : Contains the index group number (32 bit, unsigned) of the requested ADS service. This value is to be found in the ADS table of the addressed device.
IDXOFFS : Contains the index offset number (32 bit, unsigned) of the requested ADS service. This value is to be found in the ADS table of the addressed device.
LEN : Contains the number, in bytes, of the data to be read.
SRCADDR : Contains the address of the buffer from which the data to be written is to be fetched. The programmer is himself responsible for dimensioning the buffer to such a size that ‘LEN’ bytes can be taken from it. The buffer can be a single variable, an array or a structure, whose address can be found with the ADR operator.
WRITE : The ADS command is triggered by a rising edge at this input.
TMOUT : States the time before the function is cancelled.
BUSY : This output remains TRUE until the block has executed a command, but at the longest for the duration supplied to the ‘Timeout’ input. While Busy = TRUE, no new command will be accepted at the inputs. Please note that it is not the execution of the service but its acceptance whose time is monitored.
ERR : This output is switched to TRUE if an error occurs during the execution of a command. The command-specific error code is contained in ‘ErrorId’. If the block has a timeout error, ‘Error’ is TRUE and ‘ErrorId’ is 1861 (hexadecimal 0x745). Is reset to FALSE by the execution of a command at the inputs.
ERRID : Contains the command-specific error code of the most recently executed command. Is reset to 0 by the execution of a command at the inputs.